## Lead Times
PROCUREMENT LEAD-TIME REGISTER
Polaris DC-1 · PDC-LT-001 Rev A · order-by dates back-calculated from the need-on-site date
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Ref | Package | Equipment / element | Lead time (weeks) | Need on site | Order by | Float (weeks) | Notes
LT-01 | TP-006 | 110/20 kV transformers (2 nr, 16 MVA) | 52 | 2027-01-15 | 2026-01-16 | -6.4 | NEGATIVE FLOAT — the 52-week lead time against a need date driven by the 12.03.2027 grid energisation puts the order date BEFORE the Commencement Date. Requires an advance procurement instruction or pre-award ordering, otherwise the Section 1 date is not achievable
LT-02 | TP-006 | 20 kV switchgear and protection | 38 | 2027-01-29 | 2026-05-08 | 9.6 | Protection study must be approved before energisation
LT-03 | TP-006 | Standby generators (8 nr, 2.5 MVA) | 40 | 2027-02-12 | 2026-05-08 | 9.6 | Acoustic enclosures to meet 45 dB(A) at boundary
LT-04 | TP-006 | UPS modules (16 nr, 1000 kVA) | 30 | 2027-02-26 | 2026-07-31 | 21.6 | N+1 per hall
LT-05 | TP-006 | Battery systems | 24 | 2027-03-12 | 2026-09-25 | 29.6 | Lithium-ion requires a dedicated fire strategy
LT-06 | TP-006 | Overhead busway | 20 | 2027-03-05 | 2026-10-16 | 32.6 | Per hall, phased with fit-out
LT-07 | TP-005 | Chillers (4 nr) | 26 | 2027-02-05 | 2026-08-07 | 22.6 | N+1
LT-08 | TP-005 | Dry coolers / adiabatic units (10 nr) | 22 | 2027-02-19 | 2026-09-18 | 28.6 | Winter installation constraint
LT-09 | TP-005 | CRAH units (28 nr) | 22 | 2027-03-19 | 2026-10-16 | 32.6 | 7 per hall, N+1
LT-10 | TP-005 | Waste-heat recovery plant (4 MW) | 30 | 2027-04-30 | 2026-10-02 | 30.6 | Commissioning tied to the heating season
LT-11 | TP-002 | Structural steel (fabrication) | 18 | 2026-08-14 | 2026-04-10 | 5.6 | Procurement disruption risk — see PRJ-003 lessons
LT-12 | TP-002 | Precast concrete wall panels | 16 | 2026-09-11 | 2026-05-22 | 11.6 | 2 h fire rating between halls
LT-13 | TP-003 | Acoustic louvres | 16 | 2027-01-08 | 2026-09-18 | 28.6 | Coordinated with cooling intake velocities
LT-14 | TP-007 | BMS/DCIM hardware and licences | 16 | 2027-04-02 | 2026-12-11 | 40.6 | Open protocol BACnet/IP
LT-15 | TP-007 | Suppression system (data halls) | 20 | 2027-03-26 | 2026-11-06 | 35.6 | Subject to fire engineering approval
Float is measured from the Commencement Date (2026-03-02) to the order-by date. Light-shaded rows must be ordered within the first 8 weeks of the Contract.
DARK-SHADED ROWS HAVE NEGATIVE FLOAT: the order date falls before the Commencement Date, so the item cannot be procured within the Contract period as programmed. These require an advance procurement instruction, a relaxation of the need date, or they invalidate the Section 1 completion date.