## Milestones
MILESTONE AND CONSTRAINT REGISTER
Polaris DC-1 · PDC-MS-001 Rev A · input to the baseline programme
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Ref | Milestone / constraint | Type | Date / window | Owner | Source document | Programme consequence
MS-01 | Commencement Date | Contract milestone | 2026-03-02 | Contract | PDC-PC-001 | Start of the Time for Completion
MS-02 | S1 concept design submission | Design gate | Month 1 | Contractor | PDC-ER-001 | 14-day Engineer review
MS-03 | S2 detailed design submission | Design gate | Month 4 | Contractor | PDC-ER-001 | 21-day Engineer review
MS-04 | Statutory supervisors approved | Permit condition | Before works start | Contractor | PDC-PP-001 | Works cannot start on site until approved
MS-05 | Blasting permit + pre-condition survey complete | Permit condition | Before rock excavation | Contractor | PDC-PP-001 | Gates all eastern-third excavation
MS-06 | Blasting window | Working restriction | 08:00-18:00 Mon-Fri only | Contractor | PDC-PP-001 | Productivity constraint on rock excavation
MS-07 | Long-lead HV equipment ordered | Procurement | Month 2 | Contractor | PDC-LT-001 | 52-week lead time on 110/20 kV plant
MS-08 | 110 kV outage window applied for | Third party | 16 weeks before energisation | DNO | PDC-GC-001 | Only two seasonal windows per year
MS-09 | Earliest firm grid energisation | Third party | 2027-03-12 | DNO | PDC-GC-001 | CRITICAL — precedes Section 1 completion by weeks; commissioning power depends on it
MS-10 | Tenant fit-out access to Hall 1 | Employer/Tenant | Month 12 (2027-03-02) | Tenant | PDC-ER-001 / PDC-TA-001 | Overlaps our Section 1 completion — interface risk
MS-11 | Section 1 L4 integrated systems testing | Commissioning | Month 13 | Contractor | PDC-ER-001 | Requires energisation
MS-12 | Section 1 L5 24 h load-bank test | Commissioning | Month 14 | Contractor | PDC-ER-001 | Precedes Taking Over
MS-13 | Section 1 occupancy inspection | Permit condition | Month 14 | Authority | PDC-PP-001 | Sectional occupancy permitted per hall
MS-14 | Section 1 Taking Over | Contract milestone | 2027-05-02 | Contract | PDC-SC-001 | Delay damages EUR 18,000/day
MS-15 | Section 2 Taking Over | Contract milestone | 2027-07-02 | Contract | PDC-SC-001 | Delay damages EUR 12,000/day
MS-16 | District heating boundary works complete | Third party | 2027-08-31 | Offtaker | PDC-DH-001 | Interface obligation
MS-17 | Waste-heat 72 h witnessed delivery test | Third party | Heating season Oct-Apr only | Offtaker | PDC-DH-001 | CRITICAL — seasonal window; a miss waits for the next season
MS-18 | Section 3 Taking Over | Contract milestone | 2027-10-02 | Contract | PDC-SC-001 | Delay damages EUR 12,000/day
MS-19 | Section 4 Taking Over / whole of the Works | Contract milestone | 2028-01-02 | Contract | PDC-SC-001 | Delay damages EUR 10,000/day
MS-20 | Generator testing window | Working restriction | 09:00-16:00 Mon-Fri | Contractor | PDC-PP-001 | Constrains commissioning of standby generation
MS-21 | Archaeology watching brief (if triggered) | Risk | On discovery, NW corner | Authority | PDC-PP-001 / PDC-SS-001 | Stop-work in the affected area; no float allowance
MS-22 | Night-time noise limit 45 dB(A) NE boundary | Working restriction | Continuous | Contractor | PDC-PP-001 | Limits night working near the residential boundary