## Summary
BILL OF QUANTITIES — SUMMARY
Polaris DC-1 — Aviapolis Data Campus, Phase 1 · PDC-BOQ-001 Rev A · quantities derived from the drawing geometry
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Section | Description | Tender package | Amount (EUR) | % of total | Notes
A | Preliminaries & General Requirements | TP — main contract | 6006000 | 6.5% | see sheet A
B | Earthworks, Blasting, Piling & Substructure | TP-001 | 6468000 | 7% | see sheet B
C | Structure — Structural Steel & Precast Concrete | TP-002 | 8778000 | 9.5% | see sheet C
D | Envelope — Cladding, Roofing & Louvres | TP-003 | 5544000 | 6% | see sheet D
E | Architectural Finishes & Data Hall Containment | TP-004 | 4620000 | 5% | see sheet E
F | Mechanical — Chillers, Dry Coolers, CRAH & Pipework | TP-005 | 22176000 | 24% | see sheet F
G | Electrical — HV/MV, Transformers, UPS & Generators | TP-006 | 27720000 | 30% | see sheet G
H | ELV, BMS/DCIM, Fire Detection & Suppression | TP-007 | 5082000 | 5.5% | see sheet H
I | External Works, Security & Fibre Entry | TP-008 | 3696000 | 4% | see sheet I
J | Commissioning & Handover (L1-L5) | TP — main contract | 2310000 | 2.5% | see sheet J
| ACCEPTED CONTRACT AMOUNT |  | 92400000 | 100%

## A Preliminaries & General
SECTION A — Preliminaries & General Requirements
Polaris DC-1 · Bill of Quantities · tender package TP — main contract
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
A.01 | Site establishment, offices, welfare and hoarding | item | 1 | 1141828.7743 | 1141828.77
A.02 | Site management, supervision and QA/QC staff (22 months) | month | 22 | 92894.5444 | 2043679.98
A.03 | Temporary power, water and telecoms | item | 1 | 329001.5113 | 329001.51
A.04 | Tower and mobile cranage, hoisting and access | item | 1 | 948298.4736 | 948298.47
A.05 | Insurances, bonds and guarantees | item | 1 | 599943.9323 | 599943.93
A.06 | Site security during construction | month | 22 | 14030.9468 | 308680.83
A.07 | Environmental controls, vibration and noise monitoring | item | 1 | 256427.6485 | 256427.65
A.08 | Statutory supervisors (vastaava työnjohtaja, KVV, IV) | item | 1 | 203206.8158 | 203206.82
A.09 | Design development and risk allowance | item | 1 | 174932.04 | 174932.04
| TOTAL SECTION A |  |  |  | 6006000

## B Earthworks, Blasting, Pi
SECTION B — Earthworks, Blasting, Piling & Substructure
Polaris DC-1 · Bill of Quantities · tender package TP-001
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
B.01 | Site clearance, topsoil strip and disposal | m2 | 26565 | 6.3434 | 168512.26
B.02 | Bulk excavation in glacial till, cart away | m3 | 19255.5 | 27.9411 | 538020.62
B.03 | Rock excavation by blasting incl. vibration monitoring | m3 | 3213.6 | 144.9919 | 465945.85
B.04 | Excavation of unrecorded made ground, NW corner (provisional) | m3 | 1620 | 63.4339 | 102762.98
B.05 | Pad and strip foundations bearing on till | nr | 30 | 17821.9163 | 534657.49
B.06 | Direct-to-rock and rock-socketed foundations (blasting zone) | nr | 10 | 37003.1314 | 370031.31
B.07 | Ground beams and pile caps | m | 1450 | 434.9756 | 630714.6
B.08 | Ground-bearing slab 250 mm, 25 kN/m2, FM2 flatness | m2 | 12837 | 178.2192 | 2287799.4
B.09 | Sub-base, capping and geotextile | m2 | 12837 | 51.3513 | 659196.44
B.10 | Basement/trench waterproofing to substation cable basement | m2 | 1100 | 144.9919 | 159491.05
B.11 | Ground/dewatering contingency (perched water in till) | item | 1 | 362479.6542 | 362479.65
B.12 | Design development and risk allowance | item | 1 | 188388.35 | 188388.35
| TOTAL SECTION B |  |  |  | 6468000

## C Structure
SECTION C — Structure — Structural Steel & Precast Concrete
Polaris DC-1 · Bill of Quantities · tender package TP-002
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
C.01 | Structural steel frame, 65 kg/m2 — fabricate, supply, erect | t | 449.28 | 4823.6056 | 2167149.52
C.02 | Steel to MEP spine, mezzanine and plant support steelwork | t | 186 | 5114.1842 | 951238.27
C.03 | Precast concrete wall panels, 2 h fire rating between halls | nr | 256 | 6915.7719 | 1770437.6
C.04 | Precast panels to spine, substation and generator enclosure | nr | 148 | 6508.9618 | 963326.34
C.05 | In-situ RC to substation blast/fire separation walls | m3 | 640 | 743.8813 | 476084.06
C.06 | Metal deck, roof purlins and side rails | m2 | 12837 | 72.0635 | 925079.22
C.07 | Intumescent and cementitious fire protection to steel | m2 | 9800 | 47.6549 | 467018.01
C.08 | Erection, temporary works and connections | item | 1 | 801997.0752 | 801997.08
C.09 | Design development and risk allowance | item | 1 | 255669.9 | 255669.9
| TOTAL SECTION C |  |  |  | 8778000

## D Envelope
SECTION D — Envelope — Cladding, Roofing & Louvres
Polaris DC-1 · Bill of Quantities · tender package TP-003
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
D.01 | Insulated composite cladding to data halls, U = 0.17 W/m2K | m2 | 6604.8 | 185.7279 | 1226695.37
D.02 | Cladding to spine, substation, generator enclosure and admin | m2 | 5400 | 174.6726 | 943232.2
D.03 | Warm roof build-up incl. PIR insulation, U = 0.09 W/m2K | m2 | 12837 | 106.1302 | 1362393.45
D.04 | Acoustic louvres to cooling intake/discharge | m2 | 1240 | 464.3196 | 575756.37
D.05 | Personnel and equipment doors, incl. 3.0 x 3.5 m equipment doors | nr | 46 | 7517.5562 | 345807.59
D.06 | Rainwater goods, outlets and syphonic drainage | item | 1 | 425626.3454 | 425626.35
D.07 | Airtightness works and testing to q50 <= 1.0 | item | 1 | 232159.8248 | 232159.82
D.08 | Roof safety line, walkways and access hatches | item | 1 | 270853.1289 | 270853.13
D.09 | Design development and risk allowance | item | 1 | 161475.73 | 161475.73
| TOTAL SECTION D |  |  |  | 5544000

## E Architectural Finishes &
SECTION E — Architectural Finishes & Data Hall Containment
Polaris DC-1 · Bill of Quantities · tender package TP-004
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
E.01 | Data hall floor finish, anti-static sealed screed | m2 | 5000 | 99.1068 | 495533.98
E.02 | Cold-aisle containment framework and blanking (racks by Tenant) | m2 | 5000 | 164.0388 | 820194.17
E.03 | Internal partitions, linings and fire-rated boarding | m2 | 6400 | 150.3689 | 962361.17
E.04 | Suspended ceilings and painted finishes to admin/NOC block | m2 | 1250 | 225.5534 | 281941.75
E.05 | Admin/NOC block fit-out incl. joinery and sanitaryware | item | 1 | 1230291.2621 | 1230291.26
E.06 | Signage, wayfinding and hall labelling | item | 1 | 281941.7476 | 281941.75
E.07 | Floor and wall finishes to plant rooms | m2 | 3900 | 105.9417 | 413172.82
E.08 | Design development and risk allowance | item | 1 | 134563.11 | 134563.11
| TOTAL SECTION E |  |  |  | 4620000

## F Mechanical
SECTION F — Mechanical — Chillers, Dry Coolers, CRAH & Pipework
Polaris DC-1 · Bill of Quantities · tender package TP-005
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
F.01 | Chillers, 4 nr (N+1) | nr | 4 | 547486.9656 | 2189947.86
F.02 | Dry coolers / adiabatic units, 10 nr | nr | 10 | 296125.0254 | 2961250.25
F.03 | CRAH units, 7 per hall (N+1) | nr | 28 | 80057.0563 | 2241597.58
F.04 | Primary and secondary pump sets incl. inverters | nr | 12 | 66283.7993 | 795405.59
F.05 | Buffer vessels, pressurisation and glycol dosing | item | 1 | 800570.5629 | 800570.56
F.06 | Chilled water pipework, welded and pre-insulated | m | 2850 | 662.838 | 1889088.28
F.07 | Valves, strainers, commissioning sets and instrumentation | item | 1 | 2134854.8344 | 2134854.83
F.08 | Waste-heat recovery plant, 4 MW at 70 C flow | item | 1 | 3753212.5314 | 3753212.53
F.09 | Heat recovery pipework to site boundary chamber | m | 260 | 1239.5931 | 322294.21
F.10 | Ventilation, smoke extract and comfort cooling to ancillary areas | item | 1 | 2496402.8305 | 2496402.83
F.11 | Water treatment and adiabatic make-up (WUE <= 0.25 L/kWh) | item | 1 | 895261.7047 | 895261.7
F.12 | Thermal insulation, identification and testing | item | 1 | 1050210.8459 | 1050210.85
F.13 | Design development and risk allowance | item | 1 | 645902.91 | 645902.91
| TOTAL SECTION F |  |  |  | 22176000

## G Electrical
SECTION G — Electrical — HV/MV, Transformers, UPS & Generators
Polaris DC-1 · Bill of Quantities · tender package TP-006
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
G.01 | 110/20 kV transformers, 2 nr at 16 MVA (N+1) | nr | 2 | 1232454.1744 | 2464908.35
G.02 | 110 kV termination, metering and protection | item | 1 | 1524900.9277 | 1524900.93
G.03 | 20 kV ring main switchboard and protection relays | panel | 14 | 100267.4583 | 1403744.42
G.04 | Hall substations 20/0.4 kV, 4 nr at 3.3 MVA | nr | 4 | 279913.321 | 1119653.28
G.05 | Standby generators, 8 nr at 2.5 MVA, acoustic enclosure | nr | 8 | 1028785.8999 | 8230287.2
G.06 | Generator paralleling, ATS and control system | item | 1 | 1378677.5511 | 1378677.55
G.07 | Bulk fuel storage, bunding, polishing and day tanks (48 h) | item | 1 | 1232454.1744 | 1232454.17
G.08 | UPS modules, 4 per hall at 1000 kVA (N+1) | nr | 16 | 194268.2004 | 3108291.21
G.09 | Battery systems, 5 min autonomy at full load, per hall | nr | 4 | 275735.5102 | 1102942.04
G.10 | LV main switchboards and distribution | nr | 8 | 154578.9982 | 1236631.99
G.11 | Overhead busway to rack PDUs | m | 960 | 647.5607 | 621658.24
G.12 | Containment, cabling, small power and lighting | item | 1 | 2339574.0261 | 2339574.03
G.13 | Earthing, bonding and lightning protection | item | 1 | 710227.8293 | 710227.83
G.14 | Energy metering per hall and per feed | item | 1 | 438670.1299 | 438670.13
G.15 | Design development and risk allowance | item | 1 | 807378.64 | 807378.64
| TOTAL SECTION G |  |  |  | 27720000

## H ELV, BMS-DCIM, Fire Dete
SECTION H — ELV, BMS/DCIM, Fire Detection & Suppression
Polaris DC-1 · Bill of Quantities · tender package TP-007
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
H.01 | Aspirating smoke detection to white space | m2 | 5000 | 38.2357 | 191178.34
H.02 | Addressable fire detection and alarm to remaining areas | m2 | 9450 | 23.2739 | 219938.22
H.03 | Gaseous/water-mist suppression to data halls (subject to approval) | nr | 4 | 320015.9242 | 1280063.7
H.04 | Sprinkler installation and dry risers to ancillary areas | m2 | 9450 | 28.2611 | 267067.83
H.05 | BMS incl. field devices, panels and BACnet/IP integration | item | 1 | 980828.0273 | 980828.03
H.06 | DCIM incl. per-hall power, cooling and environmental reporting | item | 1 | 531974.5233 | 531974.52
H.07 | Access control, five layers, incl. mantrap and ANPR integration | item | 1 | 598471.3387 | 598471.34
H.08 | CCTV incl. 90-day retention and analytics | item | 1 | 465477.7079 | 465477.71
H.09 | Structured cabling, meet-me room and containment | item | 1 | 398980.8925 | 398980.89
H.10 | Design development and risk allowance | item | 1 | 148019.42 | 148019.42
| TOTAL SECTION H |  |  |  | 5082000

## I External Works, Security
SECTION I — External Works, Security & Fibre Entry
Polaris DC-1 · Bill of Quantities · tender package TP-008
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
I.01 | Roads, hardstanding and service yard | m2 | 9800 | 89.5151 | 877247.74
I.02 | Perimeter fencing, detection and vehicle gates | m | 1070 | 441.8372 | 472765.84
I.03 | Gatehouse fit-out and weighbridge | item | 1 | 275431.0014 | 275431
I.04 | Stormwater attenuation, oil separators and discharge control | item | 1 | 711530.0868 | 711530.09
I.05 | Foul, water and utility connections | item | 1 | 436099.0855 | 436099.09
I.06 | Two diverse fibre entry routes and ducts | m | 1240 | 241.0021 | 298842.64
I.07 | External lighting and small power | item | 1 | 304121.7307 | 304121.73
I.08 | Landscaping and tree replacement (permit condition) | item | 1 | 212311.3969 | 212311.4
I.09 | Design development and risk allowance | item | 1 | 107650.49 | 107650.49
| TOTAL SECTION I |  |  |  | 3696000

## J Commissioning & Handover
SECTION J — Commissioning & Handover (L1-L5)
Polaris DC-1 · Bill of Quantities · tender package TP — main contract
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Item | Description | Unit | Quantity | Rate (EUR) | Amount (EUR)
J.01 | L1 factory acceptance testing, witnessed (HV, UPS, gensets, chillers) | item | 1 | 312616.4381 | 312616.44
J.02 | L2/L3 static inspection and component start-up | item | 1 | 341036.1143 | 341036.11
J.03 | L4 integrated systems testing incl. failure-mode demonstrations | section | 4 | 136414.4457 | 545657.78
J.04 | L5 integrated load-bank testing, 24 h at full Section load | section | 4 | 115302.6862 | 461210.74
J.05 | Load bank hire, fuel and power for commissioning | item | 1 | 259837.0394 | 259837.04
J.06 | As-built documentation, O&M manuals and training | item | 1 | 198937.7333 | 198937.73
J.07 | Statutory inspections and occupancy inspections per Section | section | 4 | 30855.6484 | 123422.59
J.08 | Design development and risk allowance | item | 1 | 67281.55 | 67281.55
| TOTAL SECTION J |  |  |  | 2310000

## Basis & Assumptions
BASIS OF THE BILL OF QUANTITIES
Derivation of quantities
SYNTHETIC DEMONSTRATION DATA — NOT A REAL PROJECT
Quantity | Value | Unit | Derivation
Total building footprint | 12837 | m2 | Sum of building rectangles in geometry.py
Total GFA | 14450 | m2 | Employer's Requirements area schedule (reconciled)
Data hall footprint (each) | 1728 | m2 | 72 m x 24 m — 4 bays @ 18 m x 2 bays @ 12 m
White space per hall | 1250 | m2 | Employer's Requirements section 2.1
Hall external wall area (4 halls) | 6605 | m2 | Perimeter 192 m x eaves height 8.6 m x 4
Precast panels (halls) | 256 | nr | Total hall perimeter / 3 m panel width
Structural steel | 449.28 | t | 65 kg/m2 (Basis of Design) x 6912 m2 hall footprint
Roof area | 12837 | m2 | Equal to building footprint
Footprint inside blasting zone | 2678 | m2 | Buildings east of the eastern-third boundary in geometry.py
IT load | 10 | MW | 4 halls x 2.5 MW
Site connection | 16 | MVA | Grid Connection Offer PDC-GC-001
Generators | 8 | nr | 2.5 MVA each, N+1
CRAH units | 28 | nr | 7 per hall (N+1)
UPS modules | 16 | nr | 4 per hall at 1000 kVA (N+1)
Quantities are generated from the same geometry module as the PDC-DWG drawing set, so drawings and quantities cannot diverge.