# TENDER OFFER — TP-005 MECHANICAL — CHILLERS, DRY COOLERS, CRAH & PIPEWORK

From: Ilmatek LVI Oy

Our reference: IL-7729

To: NordBuild Oy

Project: Polaris DC-1 — Aviapolis Data Campus, Phase 1, Vantaa

Date: 19 March 2026

Validity: 90 days

Synthetic demonstration data. All parties and values are fictional.

____________________________________________________________

## 1. OFFER

We are pleased to offer for the above package on the basis of the documents issued with your enquiry.

| Item | Value |
| --- | --- |
| Tender sum (excluding VAT) | EUR 22,286,880 |
| Currency | EUR |
| Programme, instruction to completion | 48 weeks |
| Validity | 90 days from the date of this offer |
| Form of subcontract | YSE 1998, subject to section 4 below |

## 2. INCLUSIONS

Chillers (4 nr, N+1) and dry coolers / adiabatic units (10 nr)

CRAH units, 7 per hall (N+1)

Chilled water pipework, pumps, buffer vessels and glycol dosing

Waste-heat recovery plant, not less than 4 MW at not less than 70 C flow, to the site boundary chamber

Ventilation, smoke extract and comfort cooling to ancillary areas

Water treatment and adiabatic make-up within WUE <= 0.25 L/kWh

Free cooling not less than 8,300 hours per year

Mechanical commissioning support to L4 and L5

## 3. EXCLUSIONS

None. Our tender sum covers the full scope of the enquiry.

## 4. QUALIFICATIONS

Free cooling 8,420 hours per year modelled on Vantaa climate data, meeting the Employer's Requirements

Includes the 4 MW / 70 C heat recovery plant and the 72-hour witnessed delivery test

Notes the offtaker will only accept the connection in the October-April heating season

## 5. EXCEPTIONS TO THE FLOW-DOWN TERMS

| Item | Our position | Note |
| --- | --- | --- |
| Performance guarantee | PUE and WUE contribution warranted, backed by 5% of subcontract sum | Supports our main contract guarantee |
| Liability cap | Subcontract sum | Acceptable |
| Payment | 45 days | Matches our inflow |

## 6. PROGRAMME AND LEAD TIMES

We require 48 weeks from instruction to completion of our works, sequenced to suit your sectional completion dates.

Long-lead items are stated in our qualifications above where relevant.

## 7. SIGNATURE

For and on behalf of Ilmatek LVI Oy

Signed: ..............................  Date: 19 March 2026