# POLARIS DC-1 — EMPLOYER'S REQUIREMENTS

Document Ref: PDC-ER-001 Rev C

Project: Polaris DC-1 — Aviapolis Data Campus, Phase 1, Vantaa, Finland

Employer: Polaris Digital Infrastructure Oy

Date: 12 January 2026

Status: Contract Document — performance specification

Synthetic demonstration data. All values are fictional.

____________________________________________________________

## 1. GENERAL

### 1.1 Nature of these Requirements

This document is a performance specification. Except where a prescriptive requirement is stated, the Contractor selects the means of compliance and carries the design responsibility for doing so. Where a figure is stated as a guarantee, it is a contractual performance requirement and not an aspiration.

### 1.2 Scope of the Works

Design, procurement, construction, testing, commissioning and handover of a 10 MW colocation data centre comprising:

four data halls, each of 2.5 MW IT load, with associated electrical and

mechanical plant rooms;

a 110/20 kV primary substation and associated switchgear building;

standby generation compound and fuel storage;

chiller and dry-cooler yard;

administration and network operations centre (NOC) block;

security gatehouse, perimeter security, external works, drainage and landscaping;

two diverse fibre entry routes and meet-me room;

district-heating waste-heat recovery plant and connection to the offtaker's

boundary.

### 1.3 Battery limits

The Contractor's scope ends at:

| Interface | Limit |
| --- | --- |
| Incoming power | Contractor's 110 kV termination within the primary substation. The network operator's line and terminations are excluded. |
| District heating | Flanged connection at the site boundary chamber. Offtaker's network is excluded. |
| Fibre | Meet-me room termination panels. Carrier tails are excluded. |
| IT equipment | Excluded. Racks, servers and containment *doors* are by the Tenant; containment framework and blanking are by the Contractor. |
| Water and foul | Connection at the south-west corner chamber. |

### 1.4 Standards

Compliance with Finnish statutory requirements is mandatory, in particular the Land Use and Building Act (132/1999), the National Building Code of Finland, SFS 6000 (low-voltage installations), SFS 6001 (high-voltage installations), and the Rescue Act. Where these Requirements refer to EN or IEC standards, the Finnish national implementation applies. Uptime Institute Tier III criteria are adopted as the resilience benchmark but certification is not required.

____________________________________________________________

## 2. THE FACILITY

### 2.1 Area schedule

| Area | GFA (m²) | Notes |
| --- | --- | --- |
| Data Hall 1 | 1,650 | 1,250 m² white space + 400 m² electrical/mechanical |
| Data Hall 2 | 1,650 | as Hall 1 |
| Data Hall 3 | 1,650 | as Hall 1 |
| Data Hall 4 | 1,650 | as Hall 1 |
| Shared MEP spine and mezzanine | 2,900 | Pipework, busway, UPS, battery rooms |
| Primary substation and switchgear building | 1,100 | 110/20 kV |
| Generator compound (enclosed) | 950 | 8 × 2.5 MVA |
| Administration and NOC block | 1,250 | Two-storey, offices, NOC, welfare |
| Security gatehouse and loading | 350 |  |
| Circulation, corridors, plant voids and ancillary | 1,300 | Spread across the buildings above |
| Total GFA | 14,450 | ±3% design tolerance |

### 2.2 Structural criteria

| Item | Requirement |
| --- | --- |
| Frame | Steel portal/braced frame, 12 m × 18 m primary grid |
| Clear internal height (white space) | 4.2 m minimum under lowest service |
| Wall construction | Precast concrete panels, minimum 2-hour fire rating between halls |
| Ground floor slab | Ground-bearing, 25 kN/m² uniform imposed load, FM2 flatness |
| Raised floor | Not required in white space — overhead containment and busway |
| Roof | Insulated warm roof, imposed load allowance for PV plus plant |
| Design life | 50 years structure, 25 years envelope |
| Snow and wind | Finnish national annex loading, Vantaa location |
| Seismic | Not applicable |

### 2.3 Envelope

| Item | Requirement |
| --- | --- |
| U-values | Wall 0.17, roof 0.09, doors 1.0 W/m²K |
| Airtightness | q50 ≤ 1.0 m³/(h·m²) |
| Acoustic | 45 dB(A) at the north-east residential boundary, night-time |
| Louvres | Weather-and-bird resistant, coordinated with cooling intake velocities |
| Fire | External wall reaction-to-fire class per National Building Code |

____________________________________________________________

## 3. ELECTRICAL REQUIREMENTS

### 3.1 Capacity and topology

| Item | Requirement |
| --- | --- |
| IT load | 2.5 MW per hall, 10 MW total |
| Design rack density | 8 kW average, 15 kW peak per rack |
| Incoming supply | 110 kV, transformed to 20 kV on site, dual 110/20 kV transformers |
| Distribution | 20 kV ring to hall substations, 400 V distribution via busway |
| Redundancy | N+1 at every level between incoming transformer and rack PDU |
| Concurrent maintainability | Any single item of plant removable for maintenance without loss of IT load |
| Standby generation | 8 × 2.5 MVA diesel, N+1 for the full site load including cooling |
| Fuel storage | 48 hours at full load, bunded, with a fuel polishing system |
| UPS | Static, double conversion, N+1 per hall, 5 minutes autonomy at full load |
| Batteries | VRLA or lithium-ion; if lithium, dedicated fire strategy required |
| Earthing | Common bonding network, TN-S |
| Metering | Per-hall and per-feed energy metering reporting to the DCIM |

### 3.2 Power quality and switching

Automatic transfer to standby generation within 10 seconds of loss of

incoming supply, with UPS carrying the load in the interim.

No single point of failure in the control system for generator start.

Generator load acceptance to be demonstrated at full block load during

commissioning.

____________________________________________________________

## 4. MECHANICAL REQUIREMENTS

### 4.1 Cooling

| Item | Requirement |
| --- | --- |
| Strategy | Indirect adiabatic free cooling as the primary mode, chilled water as backup |
| Design external condition | Summer +29 °C dry bulb / +19 °C wet bulb; winter −29 °C |
| White space supply temperature | 24 °C ± 1.5 K at rack inlet |
| Humidity | 20–70% RH non-condensing |
| Redundancy | N+1 per hall, concurrently maintainable |
| Free cooling hours | ≥ 8,300 hours per year without mechanical assistance |
| Air management | Cold-aisle containment, overhead supply |
| Pipework | Pre-insulated, welded, pressure tested; glycol concentration per winter design |
| Water use | Adiabatic make-up limited to 12,000 m³/year site-wide (WUE constraint) |

### 4.2 Waste-heat recovery

Heat recovery plant shall deliver not less than 4 MW thermal at a flow temperature of not less than 70 °C to the boundary connection, available whenever site IT load exceeds 40%. The recovery plant shall not compromise the cooling redundancy or the PUE guarantee. Refer to PDC-DH-001.

### 4.3 Performance guarantees

| Guarantee | Value | Basis of demonstration |
| --- | --- | --- |
| Annualised PUE | ≤ 1.25 | Calculated per EN 50600-4-2 from 12 months of metered data; interim demonstration at Tests after Completion using the agreed load-bank profile |
| Facility availability | 99.982% (Tier III equivalent) | Design review plus commissioning demonstration |
| Water use effectiveness | ≤ 0.25 L/kWh | Metered |
| Acoustic | 45 dB(A) at north-east boundary at night | Measurement per SFS standard |

____________________________________________________________

## 5. FIRE, LIFE SAFETY AND SECURITY

| Item | Requirement |
| --- | --- |
| Detection | Aspirating smoke detection in white space, addressable system elsewhere |
| Suppression — white space | Inert gas or water-mist, subject to a fire engineering approval by the authority |
| Suppression — other areas | Sprinkler to National Building Code, dry riser where required |
| Compartmentation | Each hall a separate fire compartment, minimum 2 hours (EI 120) |
| Escape | Per Finnish requirements, travel distances demonstrated by the Contractor |
| Security | Perimeter fence and detection, ANPR vehicle gate, mantrap at reception, five-layer access control to white space, 90-day CCTV retention |
| Access control | Integrated with the Tenant's credentialing at handover of each Section |

____________________________________________________________

## 6. CONTROLS AND MONITORING

BMS covering all mechanical and electrical plant, open protocol (BACnet/IP).

DCIM providing per-hall power, cooling and environmental reporting, with

historical trending retained for 24 months.

Alarm hierarchy agreed with the Employer before commissioning; no unassigned

critical alarms at handover.

All setpoints, sequences and cause-and-effect matrices documented and witnessed.

____________________________________________________________

## 7. SEQUENCE, PHASING AND SECTIONAL COMPLETION

The Works are divided into four Sections. Shared infrastructure sized for the full 10 MW must be complete and commissioned as part of Section 1 — the Employer will not accept a Section 1 handover that depends on later temporary arrangements.

| Section | Scope | Time for Completion |
| --- | --- | --- |
| 1 | Hall 1, primary substation, generator compound, shared cooling spine, site access, gatehouse | Month 14 |
| 2 | Hall 2 and associated plant | Month 16 |
| 3 | Hall 3 and associated plant | Month 19 |
| 4 | Hall 4, administration/NOC block, external works, landscaping | Month 22 |

Delay Damages apply per Section as set out in PDC-SC-001. Construction of later Sections shall not interrupt the operation of any Section already taken over; the Contractor shall submit a method statement addressing live-environment working before commencing work adjacent to an operating hall.

____________________________________________________________

## 8. COMMISSIONING AND HANDOVER

Five-level commissioning is required:

| Level | Activity |
| --- | --- |
| L1 | Factory acceptance testing of critical plant (witnessed for HV, UPS, generators, chillers) |
| L2 | Site delivery and static inspection |
| L3 | Individual component start-up and functional test |
| L4 | Integrated systems testing, including black-building and failure-mode tests |
| L5 | Integrated load-bank testing to full Section load for 24 hours continuous |

Tests on Completion for each Section include L4 and L5. Tests after Completion comprise the 12-month PUE demonstration. Handover of each Section requires as-built documentation, O&M manuals, training records, statutory certificates and the occupancy inspection (käyttöönottotarkastus) for that Section.

____________________________________________________________

## 9. EMPLOYER-SUPPLIED ITEMS AND EXCLUSIONS

Supplied by the Employer or the Tenant:

IT racks, servers, network equipment and containment doors;

carrier fibre tails to the meet-me room;

the Tenant's credential database for access control;

the 110 kV line and its terminations (network operator).

The Contractor shall allow for reasonable coordination and access for the above, including Tenant fit-out access to Hall 1 from Month 12, in parallel with completion of Section 1.

____________________________________________________________

## 10. DESIGN SUBMISSIONS

| Stage | Submission | Review period |
| --- | --- | --- |
| S1 | Concept design, single-line diagrams, cooling strategy | 14 days |
| S2 | Detailed design, all disciplines, calculations | 21 days |
| S3 | Construction issue, shop drawings, schedules | 14 days |
| S4 | As-built and O&M | Per Section handover |

Review by the Engineer does not relieve the Contractor of design responsibility. The Contractor shall maintain a design tracker recording every Employer comment and its disposition, available to the Engineer at any time.

____________________________________________________________

## 11. SITE CONSTRAINTS SUMMARY

Detailed in PDC-SS-001 and PDC-PP-001. In summary:

bedrock at 4–9 m; blasting is required in the eastern third of the plot and

is subject to vibration limits and notification of neighbours;

aviation height limitation and obstacle lighting obligations;

night-time noise limit at the north-east residential boundary;

110 kV overhead line crossing the northern boundary — no crane operation within

its exclusion zone without the network operator's written permission;

single site access from Tikkurilantie, shared with an operating logistics

neighbour; deliveries restricted to 06:00–22:00 on weekdays.